## Slide 1
HEIQ / XMEMBRANE
Electro-Osmotic Water
Transport Integrated into an ERV
Coupled model • O30 operating point • Validation path
MODEL SYNTHESIS
ENGLISH DECK
SEPTEMBER 2026
A physically based screening model that links moist-air thermodynamics, passive recovery, local membrane transport and cooling-coil power.
ACTIVE ERV CORE
water transport
Net transport = EO − back-diffusion
Prepared from the controlled model description and selected final result set

## Slide 2
EXECUTIVE TAKEAWAY
The model identifies a promising—but conditional—energy window
Selected O30 operating point; active membrane integrated directly into the ERV core.
418.4
kW
Known modeled total power
Active ERV + EO + AC
125.34
kW
Conditional power window
vs. passive ERV + AC
5,899
m²
Selected active membrane area
at 1.0 V terminal voltage
23.05
%
Reduction in known modeled power
EO-on vs. EO-off
WHAT THE RESULT MEANS
The passive ERV delivers the largest established reduction: 622.66 kW versus AC-only.
EO adds 1,228.3 kg/h of incremental water-transfer duty at O30.
Reduced latent load can lower both condensate duty and compressor lift.
CLAIM BOUNDARY
This is not yet a validated net saving.
Receiver, thermal management, power electronics, manifolds and additional hardware must collectively remain below 125.34 kW.
Decision framing: validate the membrane vector and close the omitted subsystem losses before making a net-savings claim.

## Slide 3
SYSTEM COMPARISON
Three systems isolate what passive recovery and EO each contribute
1 • AC only
1,166.400 kW
Outdoor air is treated directly by the cooling coil.
BASELINE
2 • Passive ERV + AC
543.741 kW
Sensible and latent recovery reduce the coil duty before cooling.
EO OFF
3 • Active ERV + EO + AC
418.400 kW
Voltage-driven water transport is added inside the same ERV membrane.
EO ON
622.659 kW
Passive ERV reduction vs. AC only
125.340 kW
Incremental EO window vs. EO off
Do not label the full AC-only → active-ERV difference as “EO savings.”

## Slide 4
SELECTED ARCHITECTURE
EO is embedded in the ERV membrane—not added as a separate downstream stage
The cooling coil remains in the system and completes cooling and dehumidification after O30.
OUTDOOR / PROCESS AIR
Active ERV membrane
Passive sensible + latent recovery
EO transport under applied voltage
Cooling coil
Remaining sensible + latent duty
ADP / bypass-factor solution
Supply air
Final temperature and
humidity target
EXHAUST / RECEIVER AIR
counter-current flow
TRANSFERRED WATER
Physical mechanisms
HEAT
warm → cool
DIFFUSION
activity gradient
EO
ionic current drags water

## Slide 5
END-TO-END MODEL CHAIN
Local membrane physics is evaluated inside a complete HVAC energy balance
1
Moist-air states
T, RH, w, h, dew point
2
Passive ERV
sensible + latent effectiveness
3
Local membrane
EO − diffusion + films
4
Core integration
8 representative segments
5
Cooling coil
ADP, BF, condensate, COP
6
Power comparison
compressor + fans + EO + losses
Core modeling principle
Every kilogram of water removed from the process air must appear in the exhaust stream, and every included electrical load is carried into the final comparison.
Forward model: measured membrane vector → system outcome
Inverse design: required system outcome → target material region

## Slide 6
LAYER 1
Psychrometrics and passive ERV recovery set the boundary conditions
Moist-air state vector
Temperature T
Relative humidity RH
Humidity ratio w
Enthalpy h, dew point and specific volume
w = m_water / m_dry air
h ≈ 1.006T + w(2501 + 1.86T)
ṁw = ṁda (win − wout)
Passive ERV effectiveness
Sensible effectiveness εs updates temperature.
Latent effectiveness εl updates humidity ratio.
Tout = TOA − εs(TOA − Texh)
wout = wOA − εl(wOA − wexh)
Pfan = V̇ Δp / ηfan
BALANCE CHECKS
✓
Process / exhaust water balance
✓
Enthalpy balance
✓
No untreated condensation state
✓
Fan pressure-drop penalty
Output: local T and water-activity boundaries for the active membrane.

## Slide 7
LAYER 2
Net water transport is EO drag minus opposing diffusion
Nw = tw · j / F − Dw(aw) Sw(aw) · daw/dx
ELECTRO-OSMOTIC TERM
NEO = tw · j / F
Ionic current carries additional water through the membrane.
DIFFUSIVE TERM
Ndiff = −Dw Sw · daw/dx
Activity gradients can oppose the desired EO direction.
tw is an input in the current inverse-design model—not a predicted material property.
High tw values remain hypothetical until measured in vapor–membrane–vapor conditions.
Practical gross EO flux: JEO,gross ≈ 0.672 · tw · j [g m⁻² h⁻¹]

## Slide 8
LAYER 3
Voltage control couples transport to hydration-dependent resistance
dV/dx = j / σ(aw) + tw · RT/F · d ln(aw)/dx
Ohmic drop
Vohm = j · ASRmembrane
Thickness ↑ or conductivity ↓ → voltage ↑
Water polarization
Vwater = tw · RT/F · ln(ar/as)
Higher tw also raises reversible water work
Series + fixed losses
j · ASRseries + Vfixed
Electrodes, contacts and electronics matter
MATERIAL VECTOR
{ tw, D, S, σ, L, ASR }
D(aw)
water diffusivity
σ(aw)
ionic conductivity
S(aw)
differential sorption capacity
Drying can reduce σ, increase resistance, lower current and raise the required voltage.
At fixed terminal voltage, current density is solved—not freely selected.

## Slide 9
CORE INTEGRATION
Gas films and changing air states make local solutions essential
PROCESS AIR
EXHAUST AIR
1
T, w
update
2
T, w
update
3
T, w
update
4
T, w
update
5
T, w
update
6
local
solve
7
T, w
update
8
T, w
update
Nw = Ks(as,bulk − as,surface)
Ai = ṅw,i / Nw,i
P EO = Σ Vi ji Ai
Nw = Kr(ar,surface − ar,bulk)
Illustrative boundary case: 16.80 mg/h gross Faraday rate → 12.37 mg/h net (73.6%) after films and back-diffusion.

## Slide 10
HVAC LINKAGE
Pre-drying can reduce condensate duty and improve compressor COP
Active ERV outlet
Lower w before coil
Coil ADP solution
BF mixes inlet and ADP states
Cooling load
ṁda(hin − hoff-coil)
Variable COP
scaled Carnot relation
Electrical power
Qcool / COP + reheat
COIL EQUATIONS
woff = BF · win + (1 − BF) · wADP
ṁcond = ṁda(win − woff)
DOUBLE BENEFIT
✓
Less water must be condensed
✓
Higher evaporating temperature may increase COP
The coil remains necessary at O30.

## Slide 11
SELECTED OPERATING POINT
O30 is an intermediate humidity state—not the final supply condition
Passive ERV outlet
13.215
g/kg dry air
O30 active ERV outlet
8.886
g/kg dry air
Final target: 20°C / 50% RH*
≈ 7.3
g/kg dry air
ACTIVE ERV
COOLING COIL
Interpretation
EO removes most of the remaining moisture after passive recovery; the coil still cools and dehumidifies to the final supply state.
*Approximate humidity ratio at 101.3 kPa; the model uses the exact psychrometric state.

## Slide 12
POWER ACCOUNTING
Known power falls by 125.34 kW versus the same ERV with EO switched off
AC only
1166.400 kW
Passive ERV + AC
543.741 kW
Active ERV + EO + AC
418.400 kW
0
200
400
600
800
1000
1200
Known electrical power [kW]
Passive recovery: −622.659 kW
Incremental EO window: −125.340 kW | −23.05%

## Slide 13
O30 MASS AND POWER BALANCE
Separate total core transport from the incremental EO duty
Water transport through active ERV core
Passive 3,137.6 kg/h
EO increment
1,228.3 kg/h
Total = 4,365.9 kg/h
740
g m⁻² h⁻¹
Average total core flux
208
g m⁻² h⁻¹
EO increment / area
200–250
g m⁻² h⁻¹
Coupon-test target range
KNOWN ACTIVE-SYSTEM SPLIT
316.910
kW
remaining AC power
≈101.490
kW
included active-core and other contributions
418.400 kW
known modeled total
Unmodeled losses must fit within 125.34 kW.

## Slide 14
SELECTED RESULT FRONTIER
Deeper drying trades voltage, membrane area and system power
420
440
460
480
500
9
10
11
12
0.10 V
6,519 m²
0.10 V
8,669 m²
0.50 V
7,066 m²
1.00 V
5,758 m²
1.00 V
5,899 m²
Active ERV outlet humidity ratio [g/kg dry air]
Known total power [kW]
O30 SELECTION
8.886 g/kg
1.00 V • 5,899 m² • 418.400 kW
The optimum is not simply the lowest voltage or smallest area. Higher voltage can reduce required area while increasing electrical stress and power.
Screening area cap: 9,000 m²
Full dehumidification required at least ≈17,253 m² in the valid screening—outside the selected area cap.

## Slide 15
MODEL SCOPE
A high-value screening model—not a validated commercial module
WHAT THE MODEL IS
✓
Physically based research model
✓
1D transport through membrane thickness
✓
Segmented counter-current ERV core
✓
Coupled water balance between air streams
✓
Voltage-controlled ionic transport
✓
Reduced but realistic coil / energy model
✓
Forward + inverse-design screening tool
WHAT IT IS NOT
!
Full 2D / 3D CFD or conjugate PDE model
!
Validated commercial ERV module
!
Validated electrochemical electrode model
!
Dynamic aging, fouling or durability model
!
Proof that high tw is achievable in vapor
!
Closed receiver / drainage / heat-rejection design
!
CAPEX or lifecycle-cost model
Use the model to define the experiment and the material target—not to skip them.

## Slide 16
VALIDATION PATH
The next experiment must close transport, electrical and balance claims together
1
Polarity-dependent net water flux
Demonstrate reversible directionality and quantify net flux.
2
Effective tw in vapor
Derive from EO flux and current under representative RH.
3
Conductivity / ASR at the same RH
Measure the electrical state that actually supports the flux.
4
Passive back-diffusion
Run matched EO-off controls across the same activity gradient.
5
Donor / receiver closure
Mass-balance both air streams; identify saturation or film limits.
6
Stable operation at 1 V
Track current, heat, electrodes and performance over time.
Success criterion: measured membrane + hardware performance preserves a positive margin inside the 125.34 kW conditional window.

## Slide 17
CONCLUSION
The model defines a credible target.
The experiment must decide whether it is real.
SYSTEM
418.4 kW known modeled total at O30
MARGIN
125.34 kW conditional window vs. passive ERV + AC
HARDWARE
5,899 m² active membrane at 1 V
MATERIAL
Inverse-design vector still requires vapor validation
RECOMMENDED NEXT MOVE
Build the vapor coupon test around the incremental target:
200–250
g m⁻² h⁻¹ net, polarity-dependent water transport
paired with current, ASR, thermal and donor/receiver balance measurements.
HeiQ / XMembrane • Coupled model synthesis • September 2026

## Slide 18
APPENDIX A
Core equation map
PSYCHROMETRICS
h = 1.006T + w(2501 + 1.86T)
ṁw = ṁda(win − wout)
PASSIVE ERV
Tout = TOA − εs(TOA − Texh)
wout = wOA − εl(wOA − wexh)
MEMBRANE FLUX
Nw = tw j/F − Dw(aw)Sw(aw) daw/dx
VOLTAGE
Vterminal = Vohm + Vwater + jASRseries + Vfixed
CORE INTEGRATION
Atotal = Σ Ai
PEO = Σ Vi ji Ai
COOLING COIL
Q̇cool = ṁda(hin − hoff)
Pcompressor = Q̇cool / COP
All balances are evaluated on a dry-air basis unless stated otherwise.

## Slide 19
APPENDIX B
Gross EO flux scales linearly with tw and current density
At j = 10 A/m², before back-diffusion and gas-film losses
tw
Gross EO flux [g m⁻² h⁻¹]
10
67
20
134
30
202
50
336
75
504
100
672
INTERPRETATION
JEO,gross ≈ 0.672 · tw · j
Gross Faradaic transport is not the useful system flux.
Back-diffusion and gas-film resistance reduce net transport.
High tw also increases the water-polarization voltage term.
The complete property vector—not a single number—sets feasibility.
Treat high tw values as design coordinates until measured.

## Slide 20
APPENDIX C
Questions the audience is likely to ask
Is tw measured for the selected membrane?
No. It is an inverse-design parameter until measured under relevant vapor conditions.
Why not use liquid-cell values directly?
Hydration, morphology, conductivity and interfacial transport can differ radically between liquid and two gas streams.
Why is not all gross EO flux useful?
Back-diffusion, activity gradients and gas films oppose or limit the desired transport.
Why is the membrane area so large?
The air flow is ~150,000 CFM while local net flux is limited; compact ERVs use many thin parallel channels to create area.
Is 23.05% a documented saving?
No. It is a reduction in the known modeled sum; all omitted losses must fit inside 125.34 kW.
What would validate the concept?
Matched polarity tests, vapor tw, RH-resolved ASR, back-diffusion, mass balance, heat and stable 1 V operation.
Controlled references: docs/MODEL_CHAIN.md and the Final Result and Decision Report (v9, 31 Aug 2026).