## Slide 1
HEIQ / XMEMBRANE
Active-ERV Model
Technical Formulation and Numerical Implementation
Peer-review deck
Control volumes • constitutive laws • boundary conditions • solver hierarchy • conservation audits • validation map
MODEL NESTING
HVAC ledger
ERV / coil endpoints
Axial two-stream core
Gas films
1D membrane BVP
local physics → system response
Model basis: controlled repository state, 02 September 2026

## Slide 2
REVIEW SCOPE
What is being reviewed—and what is not
The review target is the model formulation and implementation, not the commercial viability claim.
Reviewed model object
Steady moist-air states coupled to voltage-controlled water transport through an active membrane, integrated across an ERV core and linked to a reduced cooling-coil model.
Primary review questions
Are the governing equations internally consistent?
Are boundary conditions physically admissible?
Are numerical roots and balances closed?
Are assumptions visible?
Excluded from proof
Commercial membrane availability, long-term durability, complete receiver hardware, full thermal management, CAPEX and annual building performance.
MODEL OUTPUTS
LOCAL J AND NW
SURFACE ACTIVITIES
REQUIRED AREA
WATER BALANCE
EO POWER
REMAINING COIL POWER
Review principle: distinguish numerical verification, experimental validation and system closure.

## Slide 3
SYSTEM DEFINITION
Architecture and nested control volumes
CV-1 Outdoor / return air
bulk psychrometric states
CV-2 Active ERV core
heat + passive moisture + EO
CV-3 Cooling coil
ADP, condensate, reheat
CV-4 Power ledger
compressor + fans + EO + losses
CV-2 is itself nested
gas film
membrane x ∈ [0,L]
gas film
Conservation contract
water removed from process
= water gained by receiver
Architecture used in the selected interpretation: EO embedded in the ERV membrane; no separate post-ERV EO stage.

## Slide 4
IMPLEMENTATION HIERARCHY
Canonical numerical chain and source ownership
1
Local membrane transport (V2)
1D activity + voltage; analytical power-law or H-Nafion BVP
heiq_pre_receiver_material_analyses/heiq_pre_receiver_model.py
2
Axial process integration (V3)
local state re-solved as process humidity changes with area
src/heiq/wp1/axial/*
3
Coupled gas receiver (V12.1)
process and receiver updated with the same transported water
src/heiq/wp1/receiver/coupled_integration.py
4
Direct active-ERV screening
balanced endpoints + segmented local sizing + coil linkage
src/heiq/wp1/studies/direct_eo_erv.py
5
Study / optimisation workflows
targets, parameter sweeps, basis checks and result auditing
src/heiq/wp1/studies/* and scripts/*
Controlled model map: docs/MODEL_CHAIN.md. Research models; generated outputs should be reproducible from source.

## Slide 5
MATHEMATICAL BASIS
Coordinates, signs and conserved quantities
PROCESS / SOURCE
RECEIVER
membrane thickness L
x = 0
x = L
positive Nw and j
Primary conserved rate
Steady local water flux Nw [mol m⁻² s⁻¹].
Integrated transfer is obtained from ∫A Nw dA and must match both air-stream balances.
Humidity ratio
w = kg water / kg dry air
Water activity
aw = pv / psat(T)
Electrical sign
positive j follows source → receiver
Thermal basis
steady bulk states; no dynamic storage
Positive-flux convention is declared in heiq_pre_receiver_model.py and used by the axial/receiver APIs.

## Slide 6
AIR-SIDE PROPERTY LAYER
Moist-air states are calculated on a dry-air basis
psat(T) = Buck equation over liquid water
w = 0.621945 · pv / (p − pv)
aw = pv / psat(T)
h = 1.006T + w(2501 + 1.86T)
v = Rd T(1 + 1.6078w) / p
STATE VECTOR
{ T, RH, w, h, Tdew, v, p }
RH and activity are numerically identical for ideal moist air at the same temperature basis.
Humidity ratio, not RH, is the conserved air-stream water coordinate.
The model rejects vapor pressure ≥ total pressure and negative humidity ratio.
AIRFLOW BASIS
actual inlet CFM
dry-air mass flow derived from dry-air partial pressure
or standard dry-air CFM
reference T and p explicitly declared
The basis must not change silently between cases.
Implementation: src/heiq/wp1/airside/properties.py. Saturation pressure: Buck correlation.

## Slide 7
PASSIVE REFERENCE MODEL
ERV endpoints are effectiveness-based and balance-closed
TOA,out = TOA,in − εs,eff(TOA,in − Texh,in)
wOA,out = wOA,in − εl,eff(wOA,in − wexh,in)
εeff = ε · min(1, ṁexh / ṁOA)
Endpoint closure
Receiver outlet humidity is obtained from the water balance. Receiver outlet enthalpy is obtained from the total moist-air enthalpy balance.
ACCEPTANCE CHECKS
✓
0 ≤ sensible and latent effectiveness ≤ 1
✓
positive dry-air flows and fan efficiency
✓
water-balance residual finite and closed
✓
enthalpy-balance residual finite and closed
✓
no supersaturated outlet state
✓
both-side pressure-drop fan power included
Pfan = [ṁOA vOA Δp + ṁexh vexh Δp] / ηfan
Implementation: run_erv() in src/heiq/wp1/studies/direct_eo_erv.py.

## Slide 8
EXTERNAL MASS TRANSFER
Finite gas films connect bulk air to membrane surface activity
Nw = Ks(as,bulk − as,surface)
Nw = Kr(ar,surface − ar,bulk)
DH = 2G
parallel-plate hydraulic diameter
RE = ΡUDH/Μ
flow regime
SC = Μ/(ΡDV)
momentum / vapor diffusivity
SH(RE,SC)
7.54 laminar; smooth transition; turbulent screen
KG = SHDV/DH
gas transfer coefficient
KACTIVITY = SCALE · KG · CSAT
mol m⁻² s⁻¹ per activity
Review implication
A high intrinsic membrane flux does not guarantee a high system flux. Film coefficients depend on temperature, channel gap, velocity, pressure and the selected correlation regime.
Implementation: calculate_film_state() in src/heiq/wp1/airside/properties.py.

## Slide 9
LOCAL MEMBRANE MODEL
Steady water flux combines EO drag and Fickian back-diffusion
Nw = nd(aw) · j/F − Dw(aw) Sw(aw) · daw/dx
EO contribution
NEO = nd j/F
nd (or tw) is mol H₂O transported per mol elementary charge.
Diffusive contribution
Ndiff = −Dw Sw daw/dx
The sign follows the local activity gradient and can oppose EO.
Steady-state constraint
Nw is spatially constant through a 1D membrane with no internal water source, sink or accumulation.
positive transport: process → receiver
Model class: one-dimensional, steady, isothermal within each local solve; local properties vary with water activity.
Governing equations declared in heiq_pre_receiver_material_analyses/heiq_pre_receiver_model.py.

## Slide 10
CONSTITUTIVE CLOSURE
Material properties are local functions of water activity
D(aw) = Dref (aw/aref)^pD
σ(aw) = σref (aw/aref)^pσ
S(aw) = Sref (aw/aref)^pS
B(aw) = D(aw)S(aw)
INVERSE-DESIGN VECTOR
{ nd, Dref, σref, Sref, L, pD, pσ, pS, ASRseries }
A feasible point is a simultaneous property combination—not evidence that one real material exhibits the full vector.
HYDRATION FEEDBACK
LOCAL AW ↓
Σ ↓
ASR ↑
J ↓ AT FIXED V
EO FLUX ↓
nd is an input for the material-neutral power-law model; it is not derived from D, S or σ.
The alternative H-Nafion implementation derives local hydration-dependent D, σ, S and drag from declared correlations.

## Slide 11
ELECTROCHEMICAL CLOSURE
The voltage equation contains ohmic and water-activity terms
dV/dx = j/σ(aw) + nd(aw) RT/F · d ln(aw)/dx
Membrane ohmic
Vohm = j ∫₀ᴸ dx/σ(aw)
hydration-dependent ASR
Water polarization
Vwater = ∫ nd RT/F · d ln aw
reversible activity work
Series resistance
Vseries = j · ASRseries
contacts and current collectors
Fixed voltage
Vfixed
electrode / declared lower-bound loss
Vterminal = Vohm + Vwater + Vseries + Vfixed
Applied terminal voltage is the control input; current density is the solved response.
Power accounting uses applied terminal voltage, not a nominal voltage cap.

## Slide 12
BOUNDARY-VALUE PROBLEM
Gas-film equations determine the membrane surface activities
BULK SOURCE
SURFACE SOURCE
SURFACE RECEIVER
BULK RECEIVER
Ks
1D membrane
Kr
as,surf = as,bulk − Nw/Ks
ar,surf = ar,bulk + Nw/Kr
0 < as,surf, ar,surf < 1
Physical flux bracket
Finite films impose row-specific lower and upper flux bounds before a surface reaches aw = 0 or 1.
Surface-direction audit
Midpoint and n+1 segment-boundary states are checked so a limiting end state is not hidden.
Activity bounds use ACTIVITY_EPS = 1×10⁻⁷. Surface violations fail the local solution.

## Slide 13
LOCAL SOLVER A
The power-law model reduces to a monotone scalar flux equation
R(Nw) = Nw − nd j/F + (Bref/L) ∫as,surf^ar,surf (a/aref)^(pD+pS) da = 0
EXACT POWER-LAW REDUCTION
1 derive admissible flux interval from films
2 initialize with mean-property conductance
3 update surface activities from Nw
4 evaluate exact power-law integral
5 Newton update Nw within physical bracket
6 reconstruct ASR and voltage components
7 accept only if residual and surfaces pass
WHY THIS IS USEFUL
Constant drag removes the need for a spatial BVP solve.
D, S and σ still vary locally through analytical power-law integrals.
The flux residual tolerance is evaluated explicitly.
The activity profile can be reconstructed exactly after convergence.
ASRmem = L · [∫ a^(pD+pS−pσ) da] / [σref ∫ a^(pD+pS) da]
Default screening configuration: 12 Newton flux iterations; relative flux residual tolerance 1×10⁻⁷.

## Slide 14
LOCAL SOLVER B
The H-Nafion branch solves activity and voltage as a nonlinear BVP
UNKNOWN FIELDS AND PARAMETERS
y(ξ) = [ aw(ξ), V(ξ) ]
p = [ Nw, j ]
daw/dξ = L[nd j/F − Nw]/[D S]
dV/dξ = L j/σ + nd RT/F · (1/aw)daw/dξ
ξ = x/L ∈ [0,1]
FOUR BOUNDARY CONDITIONS
aw(0) = as,bulk − Nw/Ks
aw(1) = ar,bulk + Nw/Kr
V(0) = 0
V(1) = Vapplied − Vfixed − jASRseries
Local λ(aw), D(λ,T), σ(λ,T), S(aw) and nd(λ) are evaluated inside the ODE.
SciPy solve_bvp; default tolerance 2×10⁻⁵ and maximum 400 mesh nodes. Correlation-domain validity is reported separately.

## Slide 15
VOLTAGE CONTROL
Current is obtained by a bracketed root solve at each local state
VOLTAGE → CURRENT
given Vapplied
1 set jlow = 0
2 derive jhigh from gas-film surface limit
3 solve local flux/profile at jlow and jhigh
4 verify Vapplied is bracketed
5 bisect current interval
6 re-solve local state at jmid
7 stop when |Vcalc − Vapplied| ≤ tolerance
DEFAULT NUMERICAL CONTROLS
Bisection iterations
36
Absolute voltage tolerance
2 × 10⁻⁶ V
Relative voltage tolerance
2 × 10⁻⁶
Internal search ceiling
numerical guard
INTERPRETATION
The internal current ceiling bounds the root search. It is not an engineering acceptance limit.
A legacy 21 A/m² acceptance gate has been superseded. Current density is reported as a diagnostic unless an explicit sensitivity is declared.
Voltage root implementation: solve_powerlaw_voltage_control().

## Slide 16
FAIL-CLOSED BEHAVIOR
Local states are rejected with explicit failure categories
REQUIRED FOR ACCEPTANCE
✓
voltage root bracket exists
✓
profile / scalar solve converged
✓
0 < surface activities < 1
✓
finite positive current
✓
finite positive net flux
✓
terminal-voltage reconstruction passes
REPORTED FAILURE MODES
!
below reversible voltage
!
physical/profile bracket failure
!
voltage root non-convergence
!
activity profile out of bounds
!
non-positive water flux
!
internal search ceiling encountered
Missing or failed components remain unavailable; they are not silently set to zero.
Failure mapping: status_category() and coupled_local_gate().

## Slide 17
AXIAL PROCESS INTEGRATION
The local membrane problem is re-solved as the air state changes with area
dwprocess/dA = −Mw Nw / ṁda,process
dTprocess/dA = fheat(Vj) / [ṁda cp,moist]
Thermal modes
Isothermal: dT/dA = 0.
Adiabatic upper bound: a declared fraction of local cell power heats the process air.
PREDICTOR–CORRECTOR
for each area step ΔA:
solve local state at step start
predict w and T at step end
solve local state at predicted end
halve ΔA if end state fails
integrate mean flux and mean power
shorten final step exactly at target
update air state and continue
AUDITS
✓
target event resolved
✓
water integral = air balance
✓
power integrated by area
✓
max j / min Nw retained
✓
step failure categorized
Why area is the integration coordinate
The duty is proportional to local flux × active area, and the required total area is an output.
Native derivative and local-state interfaces: src/heiq/wp1/axial/local_state.py and axial/integration.py.

## Slide 18
TWO-STREAM INTEGRATION
The same local flux updates process and receiver water balances
process direction +A
counter-current receiver
Δṁw = N̄w Mw ΔA
wP,next = wP − Δṁw/ṁP
wR,next = wR ± Δṁw/ṁR
Counter-current boundary construction
Integration starts at the process inlet paired with the receiver outlet. That receiver outlet is conditioned by the target and the global water balance.
Published only when closed
If the process target is not reached, the assumed counter-current receiver outlet is not a solved physical boundary and is returned as unavailable.
Required residuals: process balance + receiver balance + counter-current far-end boundary.
Implementation: integrate_coupled_receiver_case() in src/heiq/wp1/receiver/coupled_integration.py.

## Slide 19
SELECTED ACTIVE-ERV SCREENING PATH
Balanced endpoints are interpolated, then each segment is locally sized
1
Choose process outlet w
defines requested total water duty
2
Close receiver endpoint
same transferred water; balanced dry-air flows
3
Prescribe sensible endpoint
effectiveness-based process temperature
4
Interpolate bulk states
typically 8 counter-current segments
5
Solve local membrane
midpoints plus n+1 physical boundaries
6
Size and integrate
Ai = ṅw,i/Nw,i; P = ΣVi ji Ai
Reduced-order assumption
Bulk T and w are interpolated between balanced endpoints; they are not obtained from a conjugate axial heat-and-mass PDE.
Boundary robustness
n segments require n+1 boundary solves so midpoint-only feasibility cannot hide an end-state reversal.
Implementation: build_direct_eo_endpoints(), build_segments() and solve_segmented_transport().

## Slide 20
MODEL TOPOLOGY
Two integration paths answer different questions
PATH A • COUPLED V12.1
State-marching receiver model
Process and receiver humidity evolve step by step with area.
Local membrane problem is re-solved at start and end of each step.
Counter-current outlet is conditioned and audited at the far end.
Adaptive step halving and exact target-event shortening.
Best for target-reaching area / receiver sensitivity studies.
PATH B • DIRECT ACTIVE ERV
Endpoint-segmented screening model
Balanced process and receiver endpoints are constructed first.
Bulk states are linearly interpolated through a fixed segment count.
Each segment is sized at a representative local state.
Explicit boundary-state direction and voltage audits are added.
Best for fast architecture / material frontier screening.
Outputs from the two paths are not interchangeable unless material, geometry, receiver and numerical basis are matched.
This distinction explains why different O30 area studies can produce different—but internally valid—numbers.

## Slide 21
COOLING-COIL COUPLING
Remaining latent and sensible duty is solved from a reduced ADP model
wtarget = BF · win + (1 − BF) · wADP
hoff = BF · hin + (1 − BF) · hADP
Q̇cool = ṁda(hin − hoff)
ṁcond = ṁda(win − woff)
Pcomp = Q̇cool / COP
COP SCALING
COPCarnot = Tevap / (Tcond − Tevap)
COP = COPrated [1 + ηcons(COPCarnot/COPCarnot,rated − 1)]
Physical checks
off-coil RH ≤ 1; supply RH ≤ 1; finite COP; reheat mode explicitly declared; “none” is invalid if reheat is required.
The coil is a reduced endpoint model—not a refrigerant-cycle simulation.
Implementation: solve_coil() and _scaled_cop() in src/heiq/wp1/studies/direct_eo_erv.py.

## Slide 22
HYDRAULIC SCREEN
Membrane area is translated into channel length and fan power
Air volume flow
V̇ = ṁda · v
Total channel width
Wtot = V̇/(u g)
Channel length
ℓ = A/(Nsides Wtot)
Reynolds number
Re = ρuDh/μ
Pressure drop
laminar or Blasius screen
Fan power
Pfan = V̇Δp/ηfan
Δp = 12 μ ℓ u / g² (Re ≤ 2300)
Δp = f (ℓ/Dh) ρu²/2, f = 0.3164 Re⁻⁰·²⁵
CONSERVATIVE SELECTION
Selected active-core fan power = max(native ideal-channel estimate, declared ERV pressure-drop floor).
This is a packaging screen; manifolds, maldistribution and fouling remain outside the model.
Implementation: src/heiq/wp1/engineering/channels.py and direct_eo_core_hydraulics().

## Slide 23
ENERGY ACCOUNTING
Electrical identities are checked locally before system totals are formed
Vterminal j = Vmembrane j + j²ASRseries + Vfixed j
PEO,cell = ∫A Vterminal j dA
PEO,grid = PEO,cell / ηelectronics
Pknown = PAC + PEO,grid + Pfans + Pcommon + included losses
LEDGER DISCIPLINE
✓
component power identity checked per area step
✓
missing terms remain unavailable—not zero
✓
site / grid conversion efficiency declared
✓
common loads applied consistently to comparators
✓
system claim disabled if required component unresolved
Receiver regeneration and heat rejection are not closed in the selected gas-receiver architecture.
System savings are conditional until the full ledger is closed.
Boundary discipline is also documented in docs/SYSTEM_ENERGY_CLOSURE_STUDY.md.

## Slide 24
PARAMETER EXPLORATION
The framework supports forward prediction and inverse design
FORWARD MODEL
measured material vector + operating point
system flux, area and power
INVERSE DESIGN
target humidity, voltage and area contract
required property region
DEFAULT SCREENING DOMAINS
nd
0.3–120
log
Dref
10⁻¹²–10⁻⁹ m²/s
log
σref
0.1–50 S/m
log
L
10–100 μm
log / set
V
0.003–2.5 V
log
Sref
10⁴–10⁵ mol m⁻³ aw⁻¹
set
pD
0–4
uniform
pσ
0–8
uniform
pS
−1–2
uniform
Sampling is not a probability model unless distributions are physically justified.
Ranges shown from heiq_pre_receiver_material_analyses/config/default.json; downstream studies may override them.

## Slide 25
NUMERICAL VERIFICATION
Conservation, equivalence and convergence checks are explicit
41
selected relevant tests passed
Executed 02 Sep 2026
✓
membrane thermodynamics
✓
axial equivalence
✓
receiver API
✓
gradient closure
✓
direct active ERV
✓
O30 required-area workflow
RESIDUAL AUDITS
✓
local flux residual
✓
terminal-voltage error
✓
process water balance
✓
receiver water balance
✓
counter-current boundary
✓
segment continuity
✓
electrical component identity
STEP-HALVING AUDIT
20 m² step
10,499.7174 m²
10 m² step
10,499.6770 m²
relative difference
0.000385%
Fixed case-94 basis at receiver multiplier 3.0.
Verification ≠ experimental validation
Test command covered six relevant test modules; convergence example from docs/O30_REQUIRED_AREA_1V_v1.md.

## Slide 26
BASIS CONTROL
Published O30 numbers must be tied to their exact model contract
Study basis
Integration method
Fixed basis
Illustrative O30 area
Interpretation
Selected final-system interpretation
8-segment endpoint sizing
selected material frontier; architecture-specific endpoint assumptions
5,899 m² at 1 V
Used for the earlier 418.4 kW system interpretation
Nonlinear required-area study
coupled V12.1 target-reaching integration
legacy case-94 material + fixed channel geometry + receiver multiplier
10,499.7–12,139.9 m² at 1 V
Receiver airflow changes area and core power
Canonical local hierarchy
V2 local → V3 axial → V12.1 receiver
declared per workflow
not one universal value
Model chain; outputs depend on explicit contract
Different areas are not a contradiction when material, geometry, receiver boundary and integration method differ—but they must never be merged.
Sources: selected v9 interpretation and docs/O30_REQUIRED_AREA_1V_v1.md.

## Slide 27
ASSUMPTION LEDGER
The model is strongest where conservation is explicit—and weakest where closure is prescribed
WELL CONSTRAINED NUMERICALLY
✓
local sign convention
✓
water balances
✓
voltage reconstruction
✓
surface admissibility
✓
target-event resolution
Verification evidence
PRESCRIBED MODEL CLOSURES
!
sensible / latent effectiveness
!
power-law property shapes
!
film correlation and scale
!
segment bulk interpolation
!
scaled-Carnot COP
Sensitivity required
NOT YET EXPERIMENTALLY CLOSED
!
vapor nd for target material
!
RH-resolved ASR under load
!
electrode heat and losses
!
receiver water handling
!
manifolds / fouling / lifetime
Experimental evidence required
The inverse-design property vector is a target region, not a validated material identification.

## Slide 28
EXPERIMENTAL VALIDATION MAP
Each high-impact model term should have a direct measurement pathway
Model quantity
Experiment
Measured observable
Acceptance focus
Net EO transport Nw
matched polarity reversal + EO-off control
mass gain/loss on both gas streams
direction, repeatability, uncertainty
Effective drag nd
measure NEO and current at the same state
nd = NEO F/j
vapor-specific—not liquid-cell inferred
D(aw)S(aw)
passive activity-gradient series
steady diffusion flux vs. Δaw and L
separate films from membrane
σ(aw) / ASR
impedance or DC under representative RH
area resistance and temperature
same hydration as flux test
Gas films Ks, Kr
vary velocity and channel gap
flux response + blank-cell pressure drop
test Sh correlation and bypass
Voltage / heat ledger
simultaneous V, I and calorimetry
V components, electrical heat partition
stable operation near 1 V
Receiver closure
meter inlet/outlet humidity and any condensate
full donor/receiver water balance
saturation and removal mechanism
A coupon test should target the incremental EO duty—not the total active-core water transfer that already includes passive recovery.

## Slide 29
PEER-REVIEW CONCLUSION
The model is auditable because its balances and failure modes are explicit.
STRENGTH
Conservation, voltage closure, surface bounds and numerical statuses are enforced rather than assumed.
KEY APPROXIMATION
The selected active-ERV path interpolates balanced bulk endpoints; it is not a conjugate axial PDE.
VALIDATION GAP
The inverse-designed material vector and receiver / thermal hardware remain experimentally open.
Recommended review focus
Are the chosen constitutive ranges defensible? Is endpoint interpolation adequate? What data will close the receiver and heat ledger?
HeiQ / XMembrane • Technical formulation and numerical implementation • 02 September 2026